### Annexure B

#### (Scope of Work)

#### For

#### Supply of

#### “SUPPLY AND MAKING OF FOUNDATION BED AND EARTHING FOR GENERATOR SET AT BEML LTD”

#### Tender No. 6300031182

#### Tender Closing date:23.01.2020 16:00 Hours

#### To

## BEML Limited

Event Service Provider:

Vendor’s Time and Expenses: To be borne by the vendor

No representation would be entertained on any errors if found in the RFQ. However, vendors to bring such errors / omissions to the notice of BEML for necessary corrective action

Confidential Document: for limited circulation among the participants of e-bid event, for Annual requirement finalization for BEML to be conducted on “BEML SRM” Platform

##### Annexure B

| “SUPPLY AND MAKING OF FOUNDATION BED & EARTHING FOR GENERATOR SET AT BEML LIMITED, BANGALORE COMPLEX.” Division: BEML, Bangalore Complex |  |  |  |  |
| --- | --- | --- | --- | --- |
| Requirement Specification |  |  |  |  |
| Sl. No. | Item Name | Item Name | UOM | Quantity |
| 1. | Construction of P.C.C foundation bed Construction and making of plain cement concrete (PCC) foundation bed measuring, length 7 mtrs, width 3mtrs, in the proportion 1:2:4 of cement, fine and coarse aggregate. The foundation depth below floor / ground level shall be 0.35 mtrs and height of the bed above floor / ground level shall be 0.35 mtrs. Necessary centering and shuttering works shall be provided as required before laying concrete to keep the concrete in position. PCC mixing shall be carried out manually or by a machine. curing shall be done with wet gunny bags. This includes demolition in hard concrete, excavating soil to depth of 0.35 mtrs, length 7 mtrs and width 2.0 mtrs. The cost shall include necessary all materials and labour for completing the Job. |  | AU | 1 |
| 2. | Supply of NEUTRAL EARTHING materials Supply of NEUTRAL EARTHING materials, copper plate of size 600mm x 600mm x 3mm thick, 40mm dia GI pipe electrode, 2.5 metres length, funnel set, salt, charcoal and hardwares. |  | SET | 4.000 |
| 3 | Supply of BODY EARTHING materials Supply of BODY EARTHING materials, 400mm dia GI pipe electrode, 2.5 metr es length, funnel set, salt, charcoal and hardwares. |  | SET | 2.000 |
| 4 | Supply of 50mm x 5mm copper flat Supply of 50mm x 5mm copper flat for neutral earthing |  | M | 40.000 |
| 5 | Supply of 50mm x 5mm GI flat Supply of 50mm x 5mm GI flat for body earthing |  | M | 20.000 |
| 6 | Instn. of Neutral and Body earth pit 1 AU consists of Installation. Of 6 Nos of Neutral and Body earth pit Installation / making of Neutral earth pit and Body earth pit by excavating to a depth of 2 mtrs and width 0.35 mtrs, insertion of earth electrode, laying with alternate layers of salt / charcoal construction of chamber with MS / Cast Iron cover plates, Laying of earth flat on floor with necessary chipping chasing complete as required. |  | AU | 1 |
| SUPPLY AND MAKING OF FOUNDATION BED & EARTHING FOR GENERATOR SET AT BEML LIMITED, BANGALORE COMPLEX. GENERAL TERMS AND CONDITIONS: 1. The firm shall visit the site before submitting the offer. 2. The supply/execution of the work is subject to acceptance by our Inspection/Electrical maintenance/user department. 3. You should make good the damages caused if any during the course of work. 4. You are solely responsible for making good the damages occurring on account of any possible accident to your labour force due to failure to take safety measures. 5. In the event of any accident / injury / disablement, you shall arrange to pay the requisite compensation, legally payable to the concerned worker/dependents, and absolve BEML in case of any claims arising thereafter. 6. Necessary power and water required for carrying out the works shall be arrange by BEML Ltd., 7. Earthing resistance to be measured and indicated on all the earth pits. 8. Necessary markings for neutral and body earthing’s to be indicated separately. |  |  |  |  |
| All the above items are required in the month of February 2020 |  |  |  |  |  |