TENDER REF: 6300033610

ANNEXURE I A – COMPLIANCE TO TECHNICAL SPECIFICATIONS & CONDITIONS

Description: Supply, install & commissioning of PORTABLE 110 V DC POWER SUPPLY UNIT of 3 KW Capacity

Quantity :01 Number

Eligibility Criteria:

- The OEM or their Authorized dealers are eligible for participating in the tender.

- The authorized dealer shall submit authorization letter from their manufacturer at the time of quoting (Informative).

- The OEM shall submit relevant certificates for being a manufacturer.

| TECHNICAL INPUTS FOR DESIGN OF THE SYSTEM |  |  | COMPLIED / NOT COMPLIED / REMARKS |
| --- | --- | --- | --- |
| SCR Thyristor Controlled DC Power supply ( 3 KW) |  |  |  |
| 1 | Input Supply | 3-Phase, 415V AC ± 10%, 50 Hz ±6%. |  |
| 2 | Power supply output capacity: | 3 KW (Variable Voltage – 0 to 150V DC, Current 28 Amps DC) Output Voltage Regulations: ± 5% of output at Full load, efficiency shall be greater than or equal to 90%, output ripple factor ≤ 0.1%. The output loads consist of combination of both inductive and resistive loads and DC power supply shall meets this requirement. |  |
| 3 | The power supply shall be provided with both Input & Output 2 pole MCB control, Input supply (1-phase 230V AC) “ON” indicator, Output “ON” indicator with Voltage display meter & current display meter (Digital Meters Only). |  |  |
| 4 | The 110V DC Output shall have protection for Overload along with reverse blocking diodes on the output side (for both Positive output and Negative output terminals) |  |  |
| 5 | The power supply shall be provided with Industrial type socket for input 230V AC supply and 110V DC supply with name plates for supply along with DC polarity indication. The supplier shall supply the mating connector for industrial sockets. |  |  |
| TECHNICAL INPUTS FOR DESIGN OF THE SYSTEM |  |  | COMPLIED / NOT COMPLIED / REMARKS |
| 6 | The power conversion diodes or thyristor shall be of reputed make and all electrical components/items used shall be of reputed make. |  |  |
| 7 | The mechanical enclosure for power supply shall be of sheet metal with thick gauge material of Mild Steel with powder coated paint. |  |  |
| 8 | The power supply unit shall be compact and weight shall be less than 50kgs |  |  |
| 9 | The power supply unit shall be of portable type. The unit shall be provided with high quality, heavy duty castor wheels for movement in industrial environment. |  |  |
| 10 | Delivery | - The Equipment to be delivered to BEML, Bangalore Complex. - The firm is requested to supply Immediately from the date of receipt of PO |  |
| 11 | Guarantee | The instruments with all its accessories shall be guaranteed for a period of 12 calendar months from the date of commissioning. During the warranty period, any part found to be defective shall be repaired / replaced by the firm free of cost within 24 hours from the date of intimation of breakdown. It is the responsibility of the firm to keep stock of all necessary spare parts (especially long lead items) and should replace defective items |  |
| 12 | Commissioning | It should be entire responsibility of the firm to supply, install & commission, prove and handing over to satisfaction of BEML at free of cost |  |

| Sl. No. | TECHNICAL TERMS & CONDITIONS | COMPLIED / NOT COMPLIED / REMARKS |
| --- | --- | --- |
| 13 | After Sales Service: During breakdown, the firm should repair the set within 24 hours from the time of intimation. |  |
| 14 | Publication : The following publications to be furnished: - Operation instruction & Maintenance Manual - Calibration certificate with traceability to national / international standard. |  |
| 15 | Inspection: Inspection of the equipment’s at suppliers’ premises by BEML Engineers / Technicians before dispatch, is required. Firm to intimate BEML for the same. Final inspection and acceptance of the equipment will be done only at BEML works. |  |
| 16 | Training: The firm should impart training in operation and maintenance of the equipment to our operator / engineers at free of cost during commissioning. |  |
| 17 | Only manufacturers or their authorised dealers to quote. The authorised dealer should enclose the duly valid authorisation letter |  |
| 18 | The firm should furnish original catalogue of the equipment along with the offer. |  |